## Template
INVERTER STATION INGECON SUN MSK17 OD/OD/NA
MAINTENANCE CHECKLIST SKID INVERTER STATION |  |  |  |  | ABN2010KI04_A
PV PLANT: |  |  |  |  | VERSION: _
MODEL AND S/N POWER STATION: |  |  |  |  | POWER STATION ID:
S/N TRANSFORMER (MANUFACTURER): |  | S/N INVERTER 1: | S/N INVERTER 3 : |  | DATE:
|  | S/N INVERTER 1: | S/N INVERTER 4 :
S/N DUAL INVERTERS:
S/N SWITCHGEAR (MANUFACTURER) : |  | S/N AUXILIAR TRANSFORMER (MANUFACTURER):
S/N AIR CONDITIONER (MANUFACTURER): |  | S/N UPS (MANUFACTURER):
CONCEPT |  |  |  | MINIMUM FREQUENCY (*) | OK | NO OK | NA
(*) PERIODICITY MUST BE ADPATED TO EACH SITE, DEPENDING ON THE SPECIFIC ENVIRONMENTAL CONDITIONS. THE CHECKLIST CONSIDERS THE MINIMUM PERIODICITY FOR A STANDARD LOCATION. EACH MANUFACTURER OF EVERY SUBCOMPONENT OF THE POWER STATION MIGHT GIVE ADDITIONAL MEASURES TO BE TAKEN MORE OFTEN. MANUFACTURER MAINTENANCE MANUAL INDICATIONS SHALL ALWAYS PREVAIL TO THIS DOCUMENT
1 | DOCUMENTATION, SIGNAGE AND PPE REQUIRED
1.1 | Locate the Power Station documentation, manuals and engineering diagrams and identify the components included in the diagrams. |  |  | ANUAL
1.2 | Availability of PPE in good condition: Rescue pole, voltage tester, stool, gloves and face shield |  |  | ANUAL
1.3 | Check that all instruction and safety signs are correctly located in the Power Station. |  |  | ANUAL
2 | GENERAL STATE OF THE POWER STATION
2.1 | Check there is no rust on the metal enclosures and painting is in good condition, in the skid and electrical cabinets. If rust is detected, proceed to apply additional painting. |  |  | ANUAL
2.2 | Check presence of pollution or rain water accumulation inside the Skid and clean it if necessary |  |  | ANUAL
2.3 | Check that cable inlets to the power station are correctly sealed: DC/AC and communications |  |  | ANUAL
2.4 | Check proper operation of auxiliary services cabinet, heating, sockets, etc (if included) |  |  | ANUAL
2.5 | Check conduits and wiring status inside the power station: good aspect and no external damages |  |  | ANUAL
2.6 | Doors of equipment are OK, opening and closing is possible without interferences. Door retention system of all the equipment in open position is functional |  |  | ANUAL
2.7 | Power Station is clean in general terms |  |  | ANUAL
2.8 | Filtering Kit and syphon are not obstructed and are completelly functional |  |  | ANUAL
3 | POWER TRANSFORMER
NOTE | BEWARE! BEFORE REMOVING ANY PROTECTIVE DEVICES, ENSURE THAT NO VOLTAGE IS PRESENT!
3.1 | Perform thermal pictures of the electrical connections of the transformer, after long operation at full power. Temperatures between analog points must be similar (+/-5ºC). The thermal images must be pasted in a different sheet, named Thermal TX 1… |  |  | ANUAL
3.2 | Bus duct is duly sealed and cover is positioned and tightened correctly |  |  | ANUAL
3.3 | Check the torque of the transformer electrical connections (65Nm) |  |  | ANUAL
3.4 | Check correct state of the MV cables and LV busbars insulation and their terminals |  |  | ANUAL
3.5 | Check correct state of the protection fuses of the auxiliary services transformer |  |  | ANUAL
3.6 | Check and register the status of protection devices of the transformer (DGPT2 or others) as per relevant manual. Register the maximum oil temperature achieved ______ºC |  |  | ANUAL
3.7 | MV wiring and LV busbars are duly fixed and there are not cutting edges that could harm them. |  |  | ANUAL
3.8 | No oil leakage inside the SKID |  |  | ANUAL
3.9 | General transformer cleanliness and correct state of its enclosure (no rust or harms in transformer enclosure) |  |  | ANUAL
3.10 | Check no abnormal noises in transformer operation |  |  | ANUAL
3.11 | Check correct state of the retention bund and drain it if necessary |  |  | ANUAL
3.12 | Check correct status of earth connection according to the electrical schemes |  |  | ANUAL
4 | MV SWITCHGEAR
4.1 | SWITCHGEAR CHECKINGS
NOTE | BEWARE! BEFORE REMOVING PROTECTIONS, ENSURE THAT NO VOLTAGE IS PRESENT AT ENERGIZED POINTS
4.1.1 | Perform thermal pictures of the electrical connections of the switchgear, after long operation at full power. Temperatures between analog points must be similar (+/-5ºC). The thermal images must be pasted in a different sheet, named Thermal RMU 1… |  |  | ANUAL
4.1.2 | Check correct tightening of the transformer position electrical connections |  |  | ANUAL
4.1.3 | Check correct state of the MV cables inside the switchgear |  |  | ANUAL
4.1.4 | Switchgear is clean inside and without external objects that might harm it |  |  | ANUAL
4.1.5 | Lubricate mobile parts that require it according to switchgear manufacturer user manual. Manipulation of disconnectors and earth disconnectors is smooth and no special strength is required for operation |  |  | ANUAL
4.1.6 | Enclosure and metal parts of the switchgear are not harmed or rusted. Apply additional painting if requested |  |  | ANUAL
4.1.7 | Operating lever of the switchgear is available and in good condition |  |  | ANUAL
4.1.8 | Check internal protection and level gauges, depending on the manufacturer and the model selectyed (gas level, as a minimum) |  |  | ANUAL
4.1.9 | Check that the retention system that keeps the door of the outdoor ecnclosure opened is functional and in good condition |  |  | ANUAL
4.2 | CHECKINGS ON THE RIS/DGPT2/DCIM PROTECTION DEVICE OF THE TRANSFORMER
4.2.1 | Check temperature alarm and trip mechanism, as well as signalization if included |  |  | ANUAL
4.2.2 | Check pressure trip mechanism and signalization if included |  |  | ANUAL
4.2.3 | Check level mechanism and signalization if included |  |  | ANUAL
4.2.4 | Set back the settings to the original value, as per electrical schemes indication |  |  | ANUAL
4.2.5 | Make sure the switchgear is tripped when required in the trip events |  |  | ANUAL
4.2.6 | Oil temperature measurement PT100 (if included) is read correctly in the remote controller |  |  | ANUAL
4.3 | CHECKINGS ON THE OVERCURRENT RELAY OR FUSES
4.3.1 | Check if settings of the relay are as indicated in the electrical schematics ,or fuses rating if applicable. Current inyection tests at customers' discrection |  |  | ANUAL
4.3.2 | If the relay has autocheking function, perform it |  |  | ANUAL
4.4 | CHECKINGS ON OTHER PROTECTIONS THAT MIGHT TRIP THE SWITCHGEAR
4.4.1 | Analize if there are other events that might trip the switchgear (remote controller operation, opening from external elements,...)and check that they do trip the switchgear |  |  | ANUAL
5 | AUXILIARY SERVICES TRANSFORMER
5.1 | Perform thermal pictures of the electrical connections of the transformer, after long operation at full power. Temperatures between analog points must be similar (+/-5ºC). The thermal images must be pasted in a different sheet, named Thermal Aux TX 1… |  |  | ANUAL
5.2 | Check the external aspect of the transformer and its enclosure: no dust or rust should be found. External painting and varnish must be in good condition |  |  | ANUAL
5.3 | Check the torque of the transformer electrical connections. |  |  | ANUAL
5.4 | Check cables and terminals proper insulation. Fuses or primary protection is operative and in good condition |  |  | ANUAL
5.5 | Winding temperature measurement PT100 (if included) is read correctly in the remote controller |  |  | ANUAL
6 | INVERTERS
6.1 | Perform the complete inverter maintenace checklist ABK2010IKI04. Check the last version at the webpage of Ingeteam. |  |  | AS PER INVERTER MANUAL
7 | AUXILIARY SERVICES/COMMUNICATIONS PANEL
7.1 | Check general status of the cabinet and its enclosure. The cabinet must not be harmed or rusted, the painting must be in good condition, door must open/close correctly. |  |  | ANUAL
7.2 | Perform thermal pictures of the electrical connections of the switchgear, after long operation at full power. Temperatures between analog points must be similar (+/-5ºC). The thermal images must be pasted in a different sheet, named Thermal LV 1… |  |  | ANUAL
7.3 | Check the torque of the external wiring connections in the terminal block. |  |  | ANUAL
7.4 | Check cables and terminals proper insulation. Correct identification of terminal blocks and wiring terminals |  |  | ANUAL
7.5 | Visual inspection of all the components inside the cabinet ans setting as per electrical engineering |  |  | ANUAL
7.6 | Cabinet cleanliness |  |  | ANUAL
7.7 | Check that the retention system that keeps the door of the outdoor ecnclosure opened is functional and in good condition |  |  | ANUAL
8 | UPS (IF INCLUDED)
8.1 | Check general aspect of the UPS : absence of dust, moisture. Clean it accordingly and replace filters/fans if requested |  |  | ANUAL
8.2 | UPS Batteries must be charged and or replaced regularly depending on site conditions. Check the batteries status as per UPS manufacturer maintenace manual and replace them if needed |  |  | ANUAL
8.3 | Charge the batteries completelly after 3months if they have not been used for a long time |  |  | EVERY 3 MONTHS
8.4 | Replace the battery when the discharge time is less than 50% of specified after full charge |  |  | EVERY 3 MONTHS
9 | AIR CONDITIONING UNIT (IF INCLUDED)
9.1 | Check the proper operation of the air conditioning unit. Temperature reached inside the cubicle/thermal drop is as expected |  |  | ANUAL
9.2 | Perform the regular maintenace tasks described by the Air Conditioner manufacturer manual |  |  | ANUAL
10 | MEASUREMENT AND INSPECTION OF EARTHING RESISTANCE
10.1 | Check that the grounding system of the power station is duly bonded as indicated in the electrical schematics |  |  | ANUAL
10.2 | Perform a dielectric test to the earthing wiring (or at least and insulation test) |  |  | ANUAL
NOTE | For measurement of grounding resistance it is necessary to switch off the MV switchgear. If the operator of the plant does not allow such procedure, this measure shall not be performed
OBSERVATIONS: (ANY RESULT THAT IS NOT OK, MUST BE NOTED DOWN IN OBSERVATIONS, EXPLAINING THE REASON WHY AND ATTACHING A PHOTO)
Note: | All the maintenance activities must be performed with the support of the Power station INSTALLATION AND OPERATION MANUAL and also the SLD. Pictures showing the internal and external status of the inverter is required to send within this filled template at the Pic 1 sheet. It is possible to add more sheet isf required. It is compulsory to send this template properly fulfilled to the local RTSS once a year in order to mantain Ingeteam's warranty. send it also this information to sat.solar.energy@ingeteam.com
INSPECTION AND TESTING EQUIPMENT
Measuring equipment |  | Identification Serial number |  | Last calibration date
REVISION |  | DATE | DESCRIPTION OF CHANGES | EXTERNAL DOC |  | INTERNAL DOC
NAME AND SIGNATURE OF PERSON RESPONSIBLE: SHOULD THE HEAD OF PLANT DECIDE, FOR ANY REASON AT ALL, NOT TO PERFORM THIS CHECKLIST BEFORE ENERGIZING, THEN HE/SHE SHOULD SIGN THIS DOCUMENT AS PROOF OF CONSENT:

## Thermal TX 1
Include here the thermal pictures of the Power Transformer

## Thermal RMU 1
Include here the thermal pictures of the Switchgear

## Thermal LV 1
Include here the thermal pictures of the LV panel

## Thermal Aux TX 1
Include here the thermal pictures of the Auxiliar Transformer